## Slide 1
Cooling Equipment
Sensor Fault Detection
LSTM classification from 30-minute sensor histories
Rishabh Srivastava | Mitul Seth | Madhav Mittal
Deep Learning Project - Section B
14 October 2026
Notes: Primary task: sensor-bias detection in one simulated AHU. Dataset https://data.openei.org/submissions/910. Student IDs: 2430010149, 2430010099, 2430010096. Do not describe this as validation of datacenter deployment.

## Slide 2
Air-handling-unit sensor faults
Cooling equipment sensor-fault detection | Simulation benchmark
2
Author-defined outdoor-air sensor biases: ±1, ±2 and ±4 °C
One simulated AHU; current condition classification while occupied and running
Notes: https://data.openei.org/submissions/910; source_inventory.pdf pages 3-7, Figure 1-2 on page 4. Source image extracted unchanged. Input temperatures are Fahrenheit; imposed bias magnitudes are Celsius.

## Slide 3
M100 source-label audit
Cooling equipment sensor-fault detection | Simulation benchmark
3
The published M100 preparation selects the batch-client scheduler-state check.
Feature removal, supervised classifiers and richer physical inputs still missed the false-alarm targets.
The equipment benchmark uses documented sensor-fault scenarios. Its labels are retained from the authors; no temperature threshold creates a target.
The M100 negative study remains in the repository as supporting research.
Notes: Supporting sources: results/task5_recovery_v1/REPORT.md; LABEL_AND_SENSOR_AUDIT.md; https://gitlab.com/ecs-lab/exadata/-/blob/main/parquet_dataset/node_aggregated_data/step2.py. Different datasets have different outcomes and prevalence; do not compare their accuracy as a matched improvement.

## Slide 4
Whole-season separation
Cooling equipment sensor-fault detection | Simulation benchmark
4
Partition | Seasons | Raw days | Scored days | Endpoints
Training | Winter + spring | 91 | 77 | 61,187
Validation | Summer | 49 | 42 | 33,432
Test | Autumn | 49 | 42 | 33,432
Windows contain 30 consecutive occupied, fan-on minutes. They never cross a source day or gap.
Scenario blocks and source days stay within one partition; no shuffled overlapping-window split
Notes: https://data.openei.org/submissions/910; results/hvac_v1/experiment_plan.json and *_cohort.csv. Metadata inspected before fitting. Source local timestamps have unspecified timezone.

## Slide 5
Sensor inputs and causal cleaning
Cooling equipment sensor-fault detection | Simulation benchmark
5
13 raw sensors and control signals
Temperatures, fan/damper/valve commands and duct pressure
6 consistency differences + 13 missing indicators = 32 input channels
Five-minute forward fill; resets at days and gaps. Training-only medians and scaling preserve missing information. Negative outdoor temperatures remain valid.
Labels, dates, seasons, scenario IDs and imposed bias levels are excluded from model inputs
Notes: Source inventory Table 1-1, page 6; src/dccad/hvac.py; preprocessing_audit.json. Damper command is a proxy, not measured mixing fraction.

## Slide 6
LSTM architecture and training
Cooling equipment sensor-fault detection | Simulation benchmark
6
Component | Fixed setting
History | 30 minutes × 32 channels
Encoder | LSTM, hidden size 32
Head | 16 units, ReLU, dropout 0.2, one logit
Optimization | Adam 0.001; batch 512; gradient clip 1
Loss / stopping | Weighted BCE; max 30 epochs; AP patience 6
Replicates | Seeds 7, 42, 123; seed 42 declared primary
Tree baseline uses latest, mean, standard deviation and slope from the same input history
Notes: src/dccad/supervised.py; scripts/train_hvac.py; experiment_plan.json. Positive weight is normal/fault training endpoint ratio, about 1/6; evaluation prevalence is unchanged.

## Slide 7
Validation stability across training seeds
Cooling equipment sensor-fault detection | Simulation benchmark
7
Chart: Summer average precision by LSTM seed
| Seed 7 | Seed 42 | Seed 123
Average precision | 0.98364 | 0.98341 | 0.9789
All three LSTM seeds pass the validation policy gate
AP mean 0.9820; sample SD 0.0027. Seed 42 remains primary before the test season.
Notes: results/hvac_v1/validation_summary.json and validation_model_comparison.csv. AP differs from trapezoidal PR-AUC. The y axis is explicitly restricted to show small AP variation.

## Slide 8
Frozen alarm policy
Cooling equipment sensor-fault detection | Simulation benchmark
8
Two high scores in three consecutive scored minutes
Logit threshold 6.967112; state resets at days and gaps
Primary validation measure | Result
Precision / reading recall | 100% / 48.66%
False-positive rate / false bursts | 0% / 0
Observable fault days detected | 36 / 36
A single uploaded window gives one score and cannot establish persistent confirmation
Notes: frozen_model.json and validation_policy_specs.json. Primary selected at validation only. Empirical zero FPR on 4,776 summer normal readings is not a deployment guarantee.

## Slide 9
Independent autumn performance
Cooling equipment sensor-fault detection | Simulation benchmark
9
Chart: Primary LSTM at the frozen policy
| Accuracy | Precision | Recall | FPR
Autumn test | 0.92818 | 0.99739 | 0.91862 | 0.014447
FPR 1.44% exceeds the original 1% goal; the final policy stays unchanged
Notes: test_summary.json; primary model lstm_seed_42 selected before final evaluation. 33,432 endpoints; fault prevalence 85.71%. All-fault baseline accuracy 85.71%, FPR 100%.

## Slide 10
Confusion counts and fault-day coverage
Cooling equipment sensor-fault detection | Simulation benchmark
10
Author label / prediction | Healthy | Fault
Healthy | 4,707 | 69
Fault | 2,332 | 26,324
69 false readings form one burst; false discovery ratio is 0.26%
35/36 observable fault days detected; 35/42 total fault days
Median delay: 392 min from midnight imposition, 2 min from the first eligible score
Notes: Primary frozen test_metrics.json; evidence_summary.json. Denominators: FPR=69/(69+4707), FDR=69/(69+26324). Delay includes midnight-to-operation downtime; no early warning established.

## Slide 11
Deep learning and tree comparison
Cooling equipment sensor-fault detection | Simulation benchmark
11
Model | Accuracy | Precision | Recall | FPR
LSTM 7 | 96.66% | 99.73% | 96.36% | 1.55%
LSTM 42 | 92.82% | 99.74% | 91.86% | 1.44%
LSTM 123 | 85.55% | 99.71% | 83.39% | 1.47%
boosting | 76.04% | 100.00% | 72.05% | 0.00%
The LSTM gains reading sensitivity; the tree has zero test false positives
Seed 42 was predeclared even though seed 7 has higher test accuracy
Notes: test_model_comparison.csv. All seeds reported under their frozen validation-selected policies. Seed 42 remains the primary; do not cherry-pick seed 7 on test.

## Slide 12
A detected sensor-fault day
Cooling equipment sensor-fault detection | Simulation benchmark
12
Chart: Frozen logit trace: 2017-11-06
| 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 380 | 400 | 420 | 440 | 460 | 480 | 500 | 520 | 540 | 560 | 580 | 600 | 620 | 640 | 660 | 680 | 700 | 720 | 740 | 760 | 780 | 800
LSTM logit | -2.1815 | -1.9191 | -2.431 | -1.8645 | -1.2538 | -0.55035 | -1.3952 | -2.0798 | -2.3092 | -2.3182 | -2.3006 | -2.2971 | -2.3051 | -2.4251 | -2.5131 | -2.5683 | -1.8463 | -0.9507 | 2.8925 | 10.1493 | 12.1936 | 12.2396 | 12.3109 | 12.5368 | 12.5527 | 12.5556 | 12.5634 | 12.5571 | 12.5404 | 12.5222 | 12.5052 | 12.4866 | 12.4524 | 12.052 | 11.9333 | 11.9007 | 11.8319 | 11.7853 | 11.7542 | 11.7393 | 11.7278
Frozen threshold | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671 | 6.9671
The report also retains the missed −1 °C day and the healthy false-alarm case
Notes: examples.json; lstm_seed_42/test_decisions.csv. Native chart uses sampled recorded logits every 20 scored readings for readability, not for metrics. Full output is retained in the repository.

## Slide 13
Scope and remaining limitations
Cooling equipment sensor-fault detection | Simulation benchmark
13
One simulated AHU and one sensor-fault family
Fault prevalence is experimental; healthy validation/test each cover one scenario week. Adjacent readings and days are correlated.
The 1.44% test FPR misses the 1% goal. No test-based threshold tuning repairs that result.
Future evidence needs separate physical units, additional fault families and new evaluation periods.
Notes: https://data.openei.org/submissions/910 and source_inventory.pdf, pages 3-7; experiment_plan.json; test_summary.json. No independence assumption across overlapping readings; no operational-prevalence or cross-equipment reliability guarantee.

## Slide 14
Demonstration and reproducibility
Cooling equipment sensor-fault detection | Simulation benchmark
14
Run Start Dashboard.bat
Replay healthy and faulted autumn days; upload a 30-minute sensor CSV; inspect the frozen model comparison.
Repository evidence includes native source labels, split manifests, model/preprocessing, training histories, saved decisions and failure examples.
Source: LBNL AFDD evaluation collection
DOI 10.25984/1824861 | data.openei.org/submissions/910
Notes: Data: https://data.openei.org/submissions/910. DOI 10.25984/1824861. Authors’ inventory pp. 3-7. Saved score/inference verification: results/hvac_v1/verification.json. Dataset switch authorized by the user; M100 studies preserved.