## Slide 1
Fault Detection
Across Four Sensors
LSTM diagnosis in a simulated air-handling unit
Rishabh Srivastava, Mitul Seth and Madhav Mittal
DSE 3170 PBL 3, Section B
October 2026
Notes: Four modeled sensor locations in a different simulated dual-duct AHU. The earlier outdoor-air benchmark remains separate. Guide: Dr. Neha V Sharma. Instructor: Mr. Santosh Rajak.

## Slide 2
Four sensor fault targets
Cooling equipment sensor fault detection
2
Model output | Sensor location
Healthy | No modeled sensor bias
Cold temperature fault | Cold supply-air temperature
Hot temperature fault | Hot supply-air temperature
Cold pressure fault | Cold supply-duct pressure
Hot pressure fault | Hot supply-duct pressure
Each source scenario contains one faulty sensor
The earlier outdoor-air detector remains a separately selectable benchmark
Notes: https://faultdetection.lbl.gov/dataset/simulated-dd-ahu-dataset/ and DOI 10.1038/s41597-023-02197-w Table 4. One imposed bias per native scenario. No simultaneous faults.

## Slide 3
Simulation dataset and recorded inputs
Cooling equipment sensor fault detection
3
17 native scenarios across a full year
One healthy case and 16 temperature or pressure bias cases
525,600 one-minute readings in each selected file
26 model inputs from 114 recorded points
Temperatures, pressure, humidity, airflow, fan speed and power
21 measurement channels and five actuator commands
Parallel scenarios share one simulated unit and calendar weather
Notes: https://faultdetection.lbl.gov/dataset/simulated-dd-ahu-dataset/. Local audit: results/multisensor_v1/archive_inventory.json, scenarios.json and training_ranges.csv. Twenty-six model inputs comprise 21 measurements plus five commands.

## Slide 4
Calendar separation and causal cleaning
Cooling equipment sensor fault detection
4
Partition | Eligible minutes | Optimization / selection
Training | 2,096,259 | 36,404 hourly windows
Validation | 463,842 | 30,877 checkpoints
Reserved test | 463,058 | Every eligible minute
30 contiguous operating readings from one scenario and source day
Training-only medians and scaling. Five-minute causal fill.
Labels, filenames and calendar identity never enter the LSTM.
Notes: results/multisensor_v2/experiment_plan.json; results/multisensor_v1/cohort_counts.csv. ISO week modulo six: zero test, five validation, other training. Matching calendar periods remain together across every scenario.

## Slide 5
LSTM and validation refinement
Cooling equipment sensor fault detection
5
Component | Configuration
Sequence encoder | 32-unit LSTM
Classification head | 16-unit ReLU, dropout 0.2, five logits
Training | Weighted cross entropy and Adam 0.001
Saved primary checkpoint | Epoch 42 of 50 epochs run
Trainable parameters | 8,293
Seed 42 stays fixed. Validation selects the model and thresholds.
Version 2 raises the epoch budget and gives healthy operation more loss weight
Notes: results/multisensor_v2/all_inputs/summary.json, experiment_plan.json. Version 1 used a twenty-epoch budget. Version 2 recorded refinement before any test scores. Four unique models total. One fixed training seed only.

## Slide 6
Training-only selection of five inputs
Cooling equipment sensor fault detection
6
Selected input | Recorded type
Hot supply fan speed | Measurement
Hot supply fan power | Measurement
Cold supply fan speed | Measurement
Cooling-coil valve command | Control command
Cold supply fan power | Measurement
Four measurements and one command
Five raw inputs reduce model size but can remove evidence needed for diagnosis
Notes: results/multisensor_v1/feature_selection.json and training_feature_ranking.csv. Whole-day grouped permutation on held-out training weeks. No validation or test used. Rankings are conditional on a tree selector and correlated variables.

## Slide 7
Reserved test performance
Cooling equipment sensor fault detection
7
Metric | Primary model
Five-class accuracy | 92.87%
Macro F1 | 89.36%
Balanced accuracy | 93.60%
Any-fault detection recall | 93.05%
Healthy false-positive rate | 2.10%
The 2.10% healthy false-positive rate exceeds the 1% goal
463,058 scored test minutes from reserved calendar weeks
Notes: results/multisensor_v2/test_summary.json. Model and policy frozen before evaluation. Test FPR target is unmet. No post-test threshold tuning.

## Slide 8
Correct sensor identification
Cooling equipment sensor fault detection
8
Chart: Precision and correct-sensor recall on reserved weeks
| Cold temp | Hot temp | Cold pressure | Hot pressure
Correct-sensor recall | 0.91031 | 0.87522 | 0.95677 | 0.95878
Precision | 0.9943 | 0.99127 | 0.9921 | 0.99502
Sensor recall ranges from 87.52% to 95.88%
Notes: results/multisensor_v2/test_by_sensor.csv. Correct-sensor recall counts only the matching faulty sensor prediction. Precision is per sensor class. Editable native chart uses unrounded saved values.

## Slide 9
Five-class confusion counts
Cooling equipment sensor fault detection
9
Source / predicted | Healthy | Cold temp | Hot temp | Cold pressure | Hot pressure
Healthy | 27,060 | 1 | 490 | 76 | 13
Cold temp | 8,821 | 94,434 | 284 | 53 | 146
Hot temp | 13,184 | 320 | 96,764 | 188 | 104
Cold pressure | 4,412 | 78 | 22 | 105,780 | 268
Hot pressure | 3,834 | 142 | 56 | 525 | 106,003
580 healthy false readings in 52 bursts across 40 active healthy days
490 false readings identify the hot-deck temperature sensor
Notes: results/multisensor_v2/test_summary.json. Native counts. First row corresponds to healthy source minutes, first column to missed fault minutes. Column order is the frozen class order.

## Slide 10
Five inputs perform worse in this study
Cooling equipment sensor fault detection
10
Candidate | Inputs | Accuracy | Macro F1 | Healthy FPR
V1 full inputs | 26 | 77.84% | 75.22% | 2.25%
V1 five inputs | 5 | 63.22% | 54.88% | 32.69%
V2 full inputs | 26 | 92.87% | 89.36% | 2.10%
V2 five inputs | 5 | 64.27% | 56.42% | 37.99%
The 26-input model retains useful evidence across the four fault targets
The result does not rule out other five-feature or engineered-feature designs
Notes: results/multisensor_v2/model_comparison.csv and frozen_model.json. All candidates disclosed. Primary family selected on validation, not chosen by test accuracy. V1 refers to original training budget and V2 to logged refinement.

## Slide 11
False alarms and remaining limits
Cooling equipment sensor fault detection
11
The false-alarm target remains unmet
Healthy FPR rises from 0.90% in validation to 2.10% on test.
The frozen test result stays unchanged after inspection.
One simulated unit and one bias at a time
No field validation or simultaneous-fault claim.
Only one training seed in this extension.
More independent evaluation data is required.
Notes: results/multisensor_v2/REPORT.md and test_summary.json. Pressure filename tokens differ from documented offset magnitudes; preserve native identifiers without making a verified magnitude claim. Source-paper DOI 10.1038/s41597-023-02197-w.

## Slide 12
Demonstration and project evidence
Cooling equipment sensor fault detection
12
Start Dashboard.bat
Select healthy operation and one case for each faulty sensor.
Replay the reserved day and inspect the sensor-specific output.
Upload the example thirty-reading CSV for fresh scoring.
Updated PBL report, editable slides and executed notebook
Saved models, score arrays and 504 reproduced validation policies
The source archive downloads separately. The saved demonstration runs offline.
Notes: https://faultdetection.lbl.gov/dataset/simulated-dd-ahu-dataset/; collection DOI 10.25984/1881324; project repository https://github.com/Mitul-dev/DataCenter-Cooling-Anomaly-Detection. Reproduction and limitations are in the updated PBL report and executed notebook.